## Report
POWER OUTPUTS
Maximum solar power generated = 2522.07 MW-th
Power cycle power output = 199.00 MW-e
Average power cycle output = 219.19 MW-e
Max. thermal power into subsurface = 1520.63 MW-th
Max. thermal power out of subsurface = 1120.63 MW-th
Charge production pump power = 0.00 MW-e
Charge injection pump power = 0.00 MW-e
Discharge production pump power = 1.78 MW-e
Discharge injection pump power = 0.71 MW-e
ANNUAL ENERGY OUTPUTS
Available solar heat = 8877.27 GWh-th
Solar heat generated = 4750.20 GWh-th
Dumped solar heat = 517.57 GWh-th
Heat delivered to low-temp. cycle = 2373.17 GWh-th
Electricity generated by low-temp. cycle = 566.82 GWh-e
Discharge condenser fan parasitic = 114.25 GWh-e
Heat delivered to thermal load = 1701.60 GWh-th
Thermal load capacity factor = 97.12 %
Heat delivered to geoTES = 3157.18 GWh-th
Heat extracted from geoTES = 2999.32 GWh-th
Max. energy stored in geoTES = 808.69 GWh-th
Max. hours of power delivery = 878.41 h
Approx. electricity from max. hours = 155.13 GWh-e
Net annual change in geoTES capacity = 0.20 GWh-th
Equivalent hours of power delivery = 0.22 h
Approx. electricity from space capacity = 0.04 GWh-e
Charge production pump consumption = 0.00 GWh-e
Charge injection pump consumption = 0.00 GWh-e
Discharge production pump consumption = 10.25 GWh-e
Discharge injection pump consumption = 4.06 GWh-e
Net electricity generated = 438.26 GWh-e
Capacity factor = 28.33 %
Number of charging production wells = 22.00
Number of charging injection wells = 55.00
Number of discharging production wells = 21.00
Number of discharging injection wells = 33.00
AREA ESTIMATES AND ASSUMPTIONS
Solar field land area estimate = 959.31 acres
Land area = mirror aperture area x 1.1, converted from m2 to acres.
Uses the Python SAM wrapper's aperture-based estimate, not a SAM land-area output.
Row spacing, roads, setbacks and infrastructure are not explicitly sized;
their allowance is represented only by the land multiplier.
GeoTES subsurface footprint estimate = 33.06 acres
Footprint = reservoir bulk volume / thickness (100 m), converted to acres.
Volume uses final-year maximum stored energy and rock sensible heat:
V = E_max / [rho_rock x cp_rock x (1 - porosity) x temperature difference].
rho_rock = 2000 kg/m3; cp_rock = 800 J/(kg K);
porosity = 0.32; temperature difference = 200 C.
Assumes uniform use of the full thickness and temperature range;
excludes pore-water heat capacity, thermal sweep and well-spacing constraints.
GeoTES acreage is not surface land required for wells or infrastructure.
Solar and GeoTES areas are not added; their footprints may overlap.
SUBSURFACE COST RESULTS
Total Exploration Cost = 2.62 M$
Permitting cost = 1.18 M$
Total Charge Drilling Cost = 0.00 M$
Charge production pump cost = 0.00 M$
Charge injection pump cost = 0.00 M$
Charge flow line cost = 0.00 M$
Total Discharge Drilling Cost = 77.78 M$
Discharge production pump cost = 2.56 M$
Discharge injection pump cost = 10.74 M$
Discharge flow line cost = 13.66 M$
Subsurface Capital Cost = 108.52 M$
Subsurface O&M Cost = 3.15 M$
Capital cost of storage = 0.13 $/kWh-th
SURFACE COST RESULTS
Solar field cost = 678.38 M$
Low-temp. power cycle cost = 329.66 M$
Surface capital cost = 1008.04 M$
Surface O&M cost = 15.12 M$
TOTAL COST RESULTS
Total capital cost = 1116.56 M$
LCOE = 0.188 $/kWh-e
LCOH = 0.005 $/kWh-th
GeoTES contribution to LCOE = 0.017 $/kWh-e
Cost results including an investment tax credit of 40.00%
Total capital cost (ITC) = 669.94 M$
LCOE (ITC) = 0.130 $/kWh-e
LCOH (ITC) = 0.003 $/kWh-th
GeoTES contribution to LCOE (ITC) = 0.012 $/kWh-e

## Run Inputs
Section | Parameter | Value
system | location | "Antelope Hills CA"
system | nY | 2
system | save_figs | true
phases | phase1 | [1, 2161]
phases | phase2 | [2161, 6553]
phases | phase3 | [6553, 8761]
operating_hours | op_hour1 | [17, 18, 19, 20, 21, 22, 23, 24]
operating_hours | op_hour2 | [17, 18, 19, 20, 21, 22, 23]
operating_hours | op_hour3 | [17, 18, 19, 20, 21, 22, 23]
csp_specs | mirror_type | "Parabolic trough"
csp_specs | nominal_dni | 950
csp_specs | solar_multiple | 2.5
csp_specs | initial_size | 100
csp_specs | csp_tmax | 250
csp_specs | csp_tmin | 100
csp_specs | csp_land_mult | 1.1
csp_costs | mirror | 105
csp_costs | land | 20
csp_costs | HX | 250
ltpc_type | ltpc_type | "HE"
ltpc_design | Wout | 199
ltpc_design | T0 | 25
ltpc_design | TIT | 250
ltpc_design | fan | 0.1
ltpc_costs | power_block | 750
ltpc_costs | HX | 250
gtes_settings | recovery | 0.95
gtes_settings | Tinit | 50
gtes_settings | Qmax | 1520.63
gtes_settings | fluid | "water"
gtes_settings | mode | "continuous"
qload | qload | 200.0
reversible_wells | reversible_wells | false
gtes_flowrate | production | 80
gtes_flowrate | injection | 40
gtes_props | rho | 2000
gtes_props | cp | 800
gtes_props | void | 0.32
gtes_props | depth | 500
gtes_props | thickness | 100
finance | lifetime | 50
finance | elec_price | 0.05
finance | inflation | 0.025
finance | irr | 0.1
finance | debt_frac | 0.6
finance | debt_ir | 0.08
finance | tax_rate | 0.28
finance | deprec | [0.2, 0.32, 0.2, 0.14, 0.14]
finance | annual_cost | [1.0, 0.0, 0.0]
finance | construc_ir | 0.0
finance | onm_rate | 0.015
finance | itc_rate | 0.4
finance | property_tax_rate | 0.0075
finance_baseline_offsets | lcoh_csp_offset | 923490000.0
finance_baseline_offsets | lcoh_om_offset | 13850000.0
finance_baseline_offsets | lcoh_sub_cap_offset | 95420000.0
finance_baseline_offsets | lcoh_sub_om_offset | 2800000.0
finance_baseline_offsets | lcoh_ein_offset | 62.5886
exploration_specs | field_type | "Greenfield"
exploration_specs | wells_count | 3
exploration_specs | target_depth | 20000
exploration_specs | cost_multiplier | 1.2
engineering | flowline_length_m | 300
engineering | piping_cost_usd_ft | 256.98
engineering | m_to_ft | 3.28084
engineering | ppi_multiplier | 1.175
engineering | base_permitting_cost | 1000000